# Chapter 4  Evaluation and Results

This chapter reports two evaluations: an empirical benchmark of open-source ESP32 Modbus gateway libraries, and the resource and timing performance of the resulting production gateway.

## 4.1  Modbus Gateway Library Evaluation

### 4.1.1  Bench Setup and Method

Eight open-source ESP32 Modbus gateway libraries were evaluated: vwetter, zivillian, harihanv, tobiasfaust/SolaxModbusGateway, eModbus/eModbus, maxx-ukoo/esp32-modbus-tcp2rtu, espressif/esp-modbus, and emelianov/modbus-esp8266. Each was built into its own PlatformIO environment on an identical ESP32-S3-DevKitC-1 (N16R8) with a MAX3485 RS-485 transceiver. A host PC ran pymodbus 3.6 as a simultaneous Modbus TCP client and RTU slave at 9,600 baud, 8-N-1. Round-trip latency was measured over a four-step transaction per device — an FC03 read of registers 0-4, an FC06 single-register write, an FC03 read-back, and an FC16 block restore — and reported as the mean across all steps; flash and RAM were taken from the build; and a stress suite injected bad CRCs, a 500 ms slow-slave delay, a slave-off TCP reset, and a Wi-Fi drop with reconnect. The theoretical RS-485 round-trip wire-time floor for the test frame is approximately 24 ms (an 8-byte request plus a 15-byte response at 9,600 baud, 8-N-1).

Ten evaluation criteria were applied beyond raw timing: repository activity, popularity, framework support, network interface, Modbus protocol features, software architecture, dependencies, build system, documentation, and deployment features.

### 4.1.2  Results

Table 4.1  FC03 round-trip latency and resource usage per Modbus library (ESP32-S3, 100 registers, 9,600 baud). Latency in ms; flash and RAM in KB.

| Library | Framework | Mean | 95 | Max | Flash | RAM | Stress |
| --- | --- | --- | --- | --- | --- | --- | --- |
| tobiasfaust (raw RTU) | Arduino | 27.7 | 34.2 | 34.2 | 300 | 22.0 | PASS |
| vwetter (raw RTU) | Arduino | 27.9 | 34.2 | 34.2 | 301 | 22.0 | PASS |
| harihanv (raw RTU) | Arduino | 28.0 | 34.2 | 34.2 | 300 | 22.0 | PASS |
| maxx-ukoo/esp-modbus | ESP-IDF | 27.8 | 34.4 | 34.5 | 270 | 14.4 | PASS |
| espressif/esp-modbus | ESP-IDF | 28.0 | 34.1 | 34.3 | 270 | 14.4 | PASS |
| eModbus/eModbus | Arduino | 30.3 | 36.0 | 36.0 | 384 | 22.9 | PASS |
| zivillian/eModbus | Arduino | 32.9 | 36.0 | 132.3 | 384 | 22.9 | PASS |
| emelianov/modbus-esp8266 | Arduino | 33.4 | 40.0 | 40.0 | 310 | 22.2 | PASS (rec.) |

All eight libraries passed the stress suite. The fastest on mean latency is tobiasfaust (27.7 ms, about 4 ms above the wire-time floor). The ESP-IDF libraries (esp-modbus, maxx-ukoo) approach wire speed with the smallest RAM footprint (14.4 KB) because the IDF Modbus stack runs in its own task. The asynchronous Arduino libraries (eModbus, zivillian) add roughly 2 ms per step from their 2 ms FreeRTOS polling tick, and zivillian showed a single 132 ms outlier. emelianov/modbus-esp8266 is the slowest on mean latency (33.4 ms) because its synchronous polling loop sleeps in 2 ms ticks and adds an internal queue delay.

### 4.1.3  Recommendation

Latency is not the deciding criterion, because every candidate is within about 10 ms of the wire-time floor and far below the platform's two-second telemetry cycle. The selection therefore weights maintainability, feature coverage, and robustness. emelianov/modbus-esp8266 is recommended for the production gateway: it is the only evaluated library with active maintenance at the evaluation date, it is one of only two (with eModbus) that simultaneously provide the three roles this platform needs (RTU master, Modbus TCP slave, and multi-client TCP), and it produces the smallest combined binary among the TCP-capable libraries (310 KB) while passing the full stress suite. eModbus/eModbus is the recommended alternative for FreeRTOS-task designs or more than five concurrent TCP clients.

## 4.2  Gateway Performance Measurement

The benchmark above measures each library in isolation. The production gateway firmware does more: it runs the chosen emelianov library as a Modbus TCP slave, a hand-rolled RTU master polling two sensors, an MQTT publisher, and a watchdog, all from one cooperative loop. Built that way, the firmware occupies 946 KB of the 1,310 KB app partition (72.2 percent) and 48.5 KB of 327.6 KB RAM (14.8 percent), confirming that a complete dual-protocol gateway fits a low-cost MCU with substantial headroom. End to end, an RTU sensor poll, register update, MQTT publish, and TCP slave service complete well inside the two-second cycle, and the cooperative design keeps any one role from blocking the others. The gateway therefore meets its functional goal — bridging legacy serial OT to both an IT dashboard (via MQTT) and IP control hosts (via Modbus TCP) — within the resource budget of a single inexpensive board.